## GENERAL
Document Title: |  | Basic Electrical Load List
Document Number: |  | Project No. |  | Area | Unit | Dis. | Doc. | Seq. | Rev.
|  | 8401 |  |  |  | EL | LST | 1001 | 1
GENERAL
|  | OPERATION DUTY: |  |  |  | CYCLE FACTOR
|  | C | (CONTINUOUS) |  |  |  | 1 | (FOR NLP, HVAC: C=0.7)
|  | I | (INTERMITTENT) |  |  |  | 0.2
|  | S | (STAND BY) |  |  |  | 0
LOAD CATEGORY:
|  |  |  | N | = NORMAL EQUIPMENT
|  |  |  | E | = ESSENTIAL EQUIPMENT
|  |  |  | V | = VITAL EQUIPMENT
KIND OF LOAD:
|  |  |  | M | = MOTORIZED LOAD
|  |  |  | F | = FIXED LOAD
* Essential equipment is defined as that whose ensures or safeguards the continuous operation of other items of equipment or installations. In case of shut-down, this equipment shall be automatically restarted and re-fed by emergency generators.
* Vital equipment is that whose operation affects personnel safety whether directly or indirectly. Incase of shut-down, this equipment shall be automatically restarted and re-fed by emergency generators.
* Electrical equipment in plant shut-down configuration are all essential and vital equipment required tobe fed by emergency generators.
* The “Rated power” is the nominal power of the equipment (name plate power).
* The “Mechanical powers” or ''Brake Horse Power (BHP)'' are the absorbed by the equipment loads (driven machine in case of motors, electrical equipment in all other cases) for normal/essential/vital services.
* The “Load Factor” is the ratio of the Absorbed Power to Rated Power of the equipment
* The “Normal/Essential & Vital absorbed powers” are the electrical absorbed powers from the power distribution system for normal/essential/vital services, taking into account the efficiency and the power factor of the relevant equipment.
ABBREIVATIONS:
|  | DOL / Y.D |  |  | : | DIRECT ON LINE / Y-D
|  | BV |  |  | : | BY VENDOR
|  | BDE |  |  | : | BY DETAIL ENGINEERING
|  | WWT |  |  | : | Waste Water Treatment
|  | DP |  |  | : | DISTRIBUTION PANEL
|  | PF |  |  | : | POWER FACTOR
00
00

## LOAS LIST
Document Title: |  |  |  | Basic Electrical Load List
Document Number : |  |  |  | Project No. |  | Area |  | Unit |  | Dis. |  | Doc. | Seq. |  | Rev.
Item | Bus No. | Tag Number | Description | BHP or Nominal Power (Kw) | Rated Power (Kw) | Voltage (V) | Nominal Speed (rpm) | Power Factor | EffIciency (%) | Load Factor | Load Category | Operation Duty | Cycle Factor | Starter Feeder Type | Kind Of Load | Is / In | Normal Absorbed Power (at run. Cond.) |  | Essential & Vital Absorbed Power (at run. Cond.)
[17 empty] | P (KW) | Q (KVAr) | P (KW) | Q (KVAr)
|  | 20-MV-SWG | 20 KV SWITCHGEAR
1 | A | TR-24-01A | 20/6.3 KV Transformer
2 | B | TR-24-01B | 20/6.3 KV Transformer
3 | B | TR-26-01A | 20/0.4 KV Transformer
4 | A | TR-26-01B | 20/0.4 KV Transformer
|  |  | TOTAL | TOTAL LOAD = 1.2 x CONNECTED LOAD (20% FOR SPARE)
|  | 6.3-MV-MCC | 6.3 KV SWITCHGEAR AND MCC
1 | A | C-1001A | Water Pump | 235 | [7 empty] | C
2 | B | C-1001B | Water Pump | 235 | [7 empty] | S
3 | B | C-4001A | Air Compressor | 410 | [7 empty] | C
4 | A | C-4001B | Air Compressor | 410 | [7 empty] | S
|  |  | TOTAL | TOTAL LOAD = 1.20 x CONNECTED LOAD (20% FOR SPARE)
|  | LV-SWG | MAIN LV SWITCHGEAR
1 | B | P-6002A | MP BFW Pump | 105 | [7 empty] | C
2 | A | P-6002B | MP BFW Pump | 105 | [7 empty] | S
3 | A | UPS-01 | AC UPS | 35 | [7 empty] | C
4 | B | UPS-02 | DC UPS | 55 | [7 empty] | S
5 | A | LP | Lighting Panel | 190 | [7 empty] | C
6 | B | MDP | Main Distribution Panel | 230 | [7 empty] | C
7 | A | CB-01 | Capacitor Bank
8 | B | CB-02 | Capacitor Bank
|  |  | TOTAL | TOTAL LOAD = 1.20 x CONNECTED LOAD (20% FOR SPARE)